## Slide 1: NICA – MPD collider complex
Speaker: K. Mukhin
NISER, Bhubaneswar 2025
India-JINR Workshop on Particle, Nuclear, Neutrino Physics and Astrophysics
10-12/11/2025
From drawing
to facility

## Slide 2: Plan of talk
NICA complex
- Some data of collider units
- Building and engineering system
MPD
- Delivery, magnet construction and some parameters
- Power supplier system
- Cryogenic infrastructure
- Magnetic field mapping

## Slide 3: Chapter 1 Nuclotron based Ion Collider fAcility NICA complex

## Slide 4: NICA complex and MPD
SPD
BM@N
Booster
Nuclotron
N I C A
MPD
Start operation in 1957
Proton beam by 10 GeV
Total weight – 36 000 Tons
NILS BOR (1961):
It took great courage, foresight, and, I would say, courage to create such a gigantic and modern instrument.

## Slide 5: Scheme of Nuclotron based Ion Collider fAcility

## Slide 6: Collider elements

## Slide 7: Assembling and tests of Collider equipment

## Slide 8: Status and plans of the collider at present day

## Slide 9: Collider building #17
Ground floor
First floor
Some data of building parameters | 
Total area of the building, m2 | 30 800
Covered area, m2 | 22150
Number of floors | 2
Building construction volume, m3 | 293500
Booster and Nuclotron
Cryogenic area
BM@N
Extracted beam
MPD
SPD

## Slide 10: Collider building #17 Ground floor
Water cooling area
One of the hallways with engineering communications on the ceiling and entrance gates
Collider tunnel
MPD hall
Ground floor parameters | 
Name | Unit, m2
Tunnel area | 5182
MPD hall | 1996,5
SPD Hall | 1996,5
Electron cooling | 106
Water cooling | 420
Power supply area | 450
Total control rooms (PS, MPD, SPD, EC…) | 180
Engineering equipment technical rooms | 395
Technical staff rooms | 450
Collider tunnel

## Slide 11: Collider building #17 First floor
First floor parameters | 
Name | Unit, m2
Electron cooling power area | 380
Water cooling | 210
Power supply area | 450
Office area, temporary collider control rooms | 220
Engineering equipment technical rooms | 5500
Technical staff rooms | 450
Example of one of the hallways
Climate control system
Cooling system
Control and office rooms
Electrical power racks

## Slide 12: Engineering systems Cooling water system
Water cooling consumers
Electrical power of the collider
MPD detector and subdetectors
Cryogenic and vacuum systems
Electron cooling systems
SPD detector
Cooling system parameters |  |  |  | 
Index number of cooling center | 1 | 2 | 3 | 4
Cooling capacity | 1335 kW | 1540 kW | 1290 kW | 453 kW
Refrigerant | Antifreeze, technical water, freon, purified water |  |  | 
Number of consumers | 10 | 10 | 9 | 2
Range of water temperature | 18 - 300C | 15 - 550C | 15 - 250C | 18 - 240C
Operation modes* | Dry cooling, cooling machine, mix mode |  |  | 
* depends on consumers
** depends on ambient temperature
Water cooling system including 4 similar cooling centers. Cooling center is complicated and uses 4 different coolants. Three operation options are available depending on the ambient temperature. This scheme allows obtaining stable temperature at the collider and detector equipment in the whole operation range regardless of the season.
Dry cooling

## Slide 13: Engineering systems Power electricity of NICA complex
Total power for NICA – 10000 kW
Include
Transformer substation – 3 un. (2500 kW each (TS 2, TS 3, TS 4))
Distribution substation DS NICA 2 -1 un. (5050 kW (supplies TS 3, TS 4))
Distribution transformer substation DTS NICA 1 – 1 un. (5050 kW (TS 2))
Situational plan of the LHEP site power supply

## Slide 14: Main power station GGP1
Upgrade of the GPP 1 was the twofold increase in electricity power.
From 22396 kV (40 MW) to 40800 kV (80 MW).
Out of the 40800 kV, 34300 kV for JINR and 6500 - for Dubna city.
The final successful commission from Rostechnadzor was carried out
Permission
for admission to the operation of a power receiving unit

## Slide 15: Cryogenic system of NICA complex Ready for the technical launch of the collider in 2025
Scheme of cryogenic NICA complex
Nuclotron
The main goal of the cryogenic department for 2025 is to ensure the cooling of all rings of the NICA complex, as well as the operation of liquid helium consumers (Cryon, MPD, magnet test stand).
Main cryogenic equipment of the
NICA complex
3 Satellite refrigerators (each cooling capacity is 2000 W at 4.5K);
2 Turbine refrigerators (each cooling capacity is 2000 W at 4.5K);
Liquefier (capacity of LHe is 1000 l/h)
Compressor complex;
Oil removal system for each of the compressor
Cryogenic LN2 and LHe pipes
Warm straight and return pipelines
*Drawings and information by A. Konstantinov

## Slide 16: Cryogenic system of NICA complex Ready for the technical launch of the collider in 2025
Satellite refrigerators in the collider building
- To cool the collider, 2 satellite helium refrigerators #2, 3 were installed in room 177 of collider building #17.
- In December 2024, they were successfully launched with cooling to the temperature of liquid helium.
- The cooling capacity of each unit is 2000 W at 4.5 K.
- In January, the refrigeration control circuits will be adjusted.
Liquefier 1000 and compressor complex
- Liquefier 1000 successfully operated at the MPD detector cooling during the run, filling 12 m3 of tank containers with liquid helium.
- The staff of the cryogenic department optimized the starting modes of the liquefier, which reduced the cooling time of the tanks and reduced energy costs.
- Liquefier has confirmed the design capacity of 1000 l/h of liquid helium.
- Two new compressors “Kaskad -110/30” successfully operated during the MPD cooling session.
Cryogenic LHe, LN2, warm straight and return pipelines
LHe
LN2
- Warm pipe is ready and tested.
- LN2 pipes are progressing as planned and will be finished in January 2025.
- LHe pipe in the west side
- LHe pipe in the east side
*Drawings and information by A. Konstantinov

## Slide 17: Histogram of cooling of collider magnets 17/10/2025
W
E

## Slide 18: Chapter 2 Multi-Purpose Detector MPD at NICA complex

## Slide 19: Magnet dimensions and delivery
The parameters for the transport of the MPD Magnet are:
• MPD Magnet weight: 80 ton
• Shipping structure weight 45 ton
• MPD Magnet dimensions without Shipping Structure (L x Ø) 8.2 x 5.9 m
• Overall dimensions (L x W x H) 9.4 x 7.2 x 6.6 m
• Total weight 125 ton
• Max tilt allowed 1 degree
Genoa (Italy) – St. Petersburg (Russia) – Ladoga and Onega lakes – Volga river – Dubna (JINR)

## Slide 20: MPD magnet construction
Parameters of the magnet | 
Magnetic field | 0,57 T
Cryostat weight and size (diameter/length) mm | 66 tons 5443/7910
Yoke weight and size (diameter/length) mm | 630 tons 6583/8970
Current Voltage | 1790 A 10V
Each pole weight | 45 tons
Total weight with support equipment | 800 tons
Homogeneity | 3*10-4

## Slide 21: Possibility of magnet moving
Three main position
Assembling position
Trim coils installation position
Beam position
Distance – 12 m
Moving time about 5 hours
Speed 2 – 3 mm/s (for the final step 0,4-0,5 mm/s)

## Slide 22: Solenoid construction
Solenoid with vacuum jacket
Solenoid without vacuum jacket
Vacuum jacket
Inner diameter is 4656 mm
Outer diameter is 5443 mm
Length is 7910 mm
Vacuum jacket (10-5 Torr in warm mode)
LN2 thermal shield (80K)
Cold mass (support cylinder for SC cables)
Superconductor cables (3 parts) total length 27 km, NbTi in pure aluminum matrix.
Cooling LN2 and LH pipes (cimmny area)
LN2 shield
6. Number of turns – 1674
7. Operation temperature 4,5 – 5,5 K
8. Operation current / Rated induction – 1,79 A / 0,5 T.
9. 12 Radial and 6 axis cold mass suspensions
10. Total heat gain – 1056 W
Parameters of solenoid
9
3
4, 5

## Slide 23: Suspension system of cold mass
Suspension system consist of 6 axils and 12 radial tie-rods.
Axis tie-rods – fixed cold mass from moving in axis direction
Maximum force of tensile/compressive is 240/89 kN. Safety factor is 4,3.
Radial tie-rods – supporting a cold mass inside vacuum vessel.
Safe against shear + bending with the sizing load of 50 kN. Safety factor 1,8.

## Slide 24: Superconductor cable
Original SC cables for MPD
Winding and tests of SC cable in ASG
SC cables parameters
SC Materials – NbTi/Cu.
Cable composition is pure aluminum matrix (4,1 x 20 mm) and inside string of Cu/SC ratio 0,9/1 (d – 1,5 mm).
Insulation – kapton tape, glass tape and epoxy resin.
Critical current (1,2 T, 4,5 K) – 6,9 kA
Cable length - 27 km.
Cable weight – 6,3 tons
LHC 27 km

## Slide 25: Power supply system

## Slide 26: Stability test of power supplies
Power supply of solenoid I = 2500A V= 10V
Power supply of TRIM1
I = 3000A V= 70V
Power supply of TRIM2
I = 1300A V= 45V

## Slide 27: Cryogenic infrastructure
Control Dewar
Refrigerator
NTCS (Nitrogen temperature correction system)
LN2 and LHe heaters
LHe pipe
Cryogenic flexible connection pipes
LN2 Tanks (2 pc)
LHe Tanks (2 pc)
LN2 transfer pipe 120 m
Warm pipes for He, N2 and instrumentation Air
Flexible warm pipes
Support system for flexible pipes

## Slide 28: Cooling process scheduled
Total cooling time – 28 days
Nitrogen mode – 14 days
Transient mode – 6 days
Helium mode – 8 days

## Slide 29: Stationary magnetic field monitors
Current 1050A

## Slide 30: Field mapper in solenoid
04/09/2025 mapper was delivered to MPD hall
16/07/2025 test mapper in Novosibirsk
From 06/10/2025 assembling and test in MPD solenoid
26-27/10/2025
Measuring in one stationary point (730,6 A)

## Slide 31: Timeline
NICA
November – December 2025 – finalisation of assembling,
cold and electrical test
Jenuary – February 2026 – first ion Xe beam in to collider
March 2026 – singl bunch and bunch collision
March – June 2026 – technical stop
From Julay 2026 – collider start operation to detectors
MPD
December 2025 – mapping, processing of results and confirmation of homogeneity (3*10-4) by 0,2 – 0,25 T
Jenuary - February 2026 – mapping of the field 0,3 – 0,5 T
From March 2026 – installetion support cylinder and start assembling detectors

## Slide 32: Thank you for attention